## alex analysis
Transducer Calibration Factor | 5 | psi/V
Density of Water | 998 | kg/m^3
Mass of water collected | 200 | lb | 90.7185 | kg
Dyno Mass | 1.502 | kg
D_1 (inlet) | 0.0508 | m
D_2 (outlet) | 0.0381 | m
D (impeller) | 0.108 | m | [6 empty] | 0.054
b (blade height at exit) | 0.009 | m | [10 empty] | 39.6564
w (blade width at exit) | 0.0085 | m
Number of blades | 5
[24 empty] | head uncertainty | [11 empty] | coeffient uncertainty
|  |  | Transducer Output |  |  | Time to collect water |  |  |  |  | Transducer Head | [5 empty] | Head coeff | flow coeff | [6 empty] | Transducer Precision |  | Transducer Bias |  | Transducer Uncertainty |  | Transducer Head Uncertainty | [8 empty] | efficiency
Pump Configuration | Valve Configuration | Pump Speed | Pump 1 | Pump 2 | Moment arm | (s) |  |  | Nominal Time | Volumetric Flow | Pump 1 | Pump 2 | Nominal Transducer Head | Corrected Head | U | v_{2r} | $\Psi$ | $\Phi$ | time stdev | t-inv | $P_t$ | $B_t$ | $\delta_t$ | $\delta_Q$ | $P_{V_{\text{tr1}}}$ | $P_{V_{\text{tr2}}}$ | $B_{V_{\text{tr1}}}$ | $B_{V_{\text{tr2}}}$ | $\delta_{V_{\text{tr1}}}$ | $\delta_{V_{\text{tr2}}}$ | $\delta_{H_t1}$ | $\delta_{H_t2}$ | $\delta_{H_t}$ | $\delta_{H}$ | $\delta_U$ | $\delta_{v_{2r}}$ | $\delta_{\Psi}$ | $\delta_{Phi}$ | Torque | efficiency | $\delta_{eff}$
|  | (RPM) | (V) | (V) | (cm) | Trial 1 | Trial 2 | Trial 3 | (s) | (m^3/s) | (m) | (m) | (m) | (m) | (m/s) | (m/s) |  |  | (s) |  | (s) | (s) | (s) | $\unit{\meter\cubed\per\second}$ | (V) | (V) | (V) | (V) | (V) | (V) | (m) | (m) | (m) | (m) | (m/s) | (m/s) |  |  | (Nm) | (%) | (\%)
Single | Fully open | 1800 | 0.75 | 0 | 8.75 | 28.55 | 28.99 | 28.79 | 28.7767 | 0.0031588 | 2.6409 | 0 | 2.6409 | 2.9084 | 10.1788 | 1.1826 | 0.27538 | 0.11618 | 0.2203 | 4.3027 | 0.54726 | 0.01 | 0.54735 | 6.0083e-05 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.035212 | 0 | 0.035212 | 0.036652 | 0 | 0.022494 | 0.0034704 | 0.0022099 | 1.2893 | 37.0105 | 0.84446 | 28.9895
Single | Partial 1 | 1800 | 0.83 | 0 | 8.5 | 30.14 | 30.51 | 30.16 | 30.27 | 0.003003 | 2.9226 | 0 | 2.9226 | 3.1643 | 10.1788 | 1.1242 | 0.29961 | 0.11045 | 0.20809 | 4.3027 | 0.51692 | 0.01 | 0.51701 | 5.1291e-05 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.035212 | 0 | 0.035212 | 0.036167 | 0 | 0.019202 | 0.0034245 | 0.0018865 | 1.2524 | 39.407 | 0.80987 | 26.593
Single | Partial 2 | 1800 | 1.43 | 0 | 7.25 | 61.12 | 60.8 | 60.86 | 60.9267 | 0.001492 | 5.0353 | 0 | 5.0353 | 5.095 | 10.1788 | 0.55855 | 0.48242 | 0.054874 | 0.1701 | 4.3027 | 0.42255 | 0.01 | 0.42267 | 1.035e-05 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.035212 | 0 | 0.035212 | 0.035222 | 0 | 0.0038748 | 0.0033349 | 0.00038068 | 1.0683 | 36.9591 | 0.36196 | 30.0409
Single | Closed | 1800 | 1.56 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 5.4931 | 0 | 5.4931 | 5.4931 | 10.1788 | 0 | 0.52011 | 0 | 0 | 4.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.035212 | 0 | 0.035212 | 0.035212 | 0 | 0 | 0.003334 | 0 | 0.66306 | 0 | -
Single | Fully open | 2700 | 1.5 | 0 | 16.5 | 18.66 | 18.93 | 18.55 | 18.7133 | 0.0048575 | 5.2818 | 0 | 5.2818 | 5.9143 | 15.2681 | 1.8185 | 0.24888 | 0.11911 | 0.19553 | 4.3027 | 0.48573 | 0.01 | 0.48583 | 0.00012611 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.035212 | 0 | 0.035212 | 0.04815 | 0 | 0.047213 | 0.0020262 | 0.0030922 | 2.4312 | 40.9166 | 1.1133 | 11.0834
Single | Partial 1 | 2700 | 1.62 | 0 | 16.5 | 19.23 | 19.23 | 18.96 | 19.14 | 0.0047492 | 5.7043 | 0 | 5.7043 | 6.3089 | 15.2681 | 1.778 | 0.26549 | 0.11645 | 0.15588 | 4.3027 | 0.38724 | 0.01 | 0.38737 | 9.6118e-05 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.035212 | 0 | 0.035212 | 0.042881 | 0 | 0.035984 | 0.0018045 | 0.0023568 | 2.4312 | 42.674 | 0.91107 | 28.326
Single | Partial 2 | 2700 | 2.94 | 0 | 14.5 | 31.15 | 31.3 | 31.22 | 31.2233 | 0.0029113 | 10.3523 | 0 | 10.3523 | 10.5795 | 15.2681 | 1.0899 | 0.44521 | 0.071385 | 0.075056 | 4.3027 | 0.18645 | 0.01 | 0.18672 | 1.741e-05 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.035212 | 0 | 0.035212 | 0.035317 | 0 | 0.0065177 | 0.0014862 | 0.00042688 | 2.1365 | 49.9173 | 0.34187 | 23.0827
Single | Closed | 2700 | 3.52 | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 12.3946 | 0 | 12.3946 | 12.3946 | 15.2681 | 0 | 0.52159 | 0 | 0 | 4.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.035212 | 0 | 0.035212 | 0.035212 | 0 | 0 | 0.0014818 | 0 | 1.2524 | 0 | -
Single | Fully open | 3600 | 2.44 | 0 | 26.5 | 14.13 | 13.93 | 14.06 | 14.04 | 0.0064744 | 8.5917 | 0 | 8.5917 | 9.7153 | 20.3575 | 2.4238 | 0.22997 | 0.11906 | 0.10149 | 4.3027 | 0.25211 | 0.01 | 0.25231 | 0.00011635 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.035212 | 0 | 0.035212 | 0.05358 | 0 | 0.043558 | 0.0012683 | 0.0021397 | 3.9047 | 41.8349 | 0.78641 | 16.1651
Single | Partial 1 | 3600 | 2.89 | 0 | 26.5 | 15.04 | 14.35 | 14.31 | 14.5667 | 0.0062403 | 10.1762 | 0 | 10.1762 | 11.2201 | 20.3575 | 2.3362 | 0.26559 | 0.11476 | 0.41041 | 4.3027 | 1.0195 | 0.01 | 1.0196 | 0.00043677 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.035212 | 0 | 0.035212 | 0.1503 | 0 | 0.16352 | 0.0035578 | 0.0080322 | 3.9047 | 46.5677 | 3.3185 | 5.4323
Single | Partial 2 | 3600 | 5.85 | 0 | 20 | 37.01 | 37.04 | 37.07 | 37.04 | 0.0024541 | 20.599 | 0 | 20.599 | 20.7604 | 20.3575 | 0.91875 | 0.49142 | 0.045131 | 0.03 | 4.3027 | 0.074524 | 0.01 | 0.075192 | 4.9819e-06 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.035212 | 0 | 0.035212 | 0.035218 | 0 | 0.0018651 | 0.00083365 | 9.1617e-05 | 2.9469 | 44.8983 | 0.11878 | 26.1017
Single | Closed | 3600 | 6.18 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 21.761 | 0 | 21.761 | 21.761 | 20.3575 | 0 | 0.51511 | 0 | 0 | 4.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.035212 | 0 | 0.035212 | 0.035212 | 0 | 0 | 0.00083351 | 0 | 1.9155 | 0 | -
Single | Manufacturer | 1800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004 | 0 | 0 | 0 | 2.58 | 10.1788 | 1.4975 | 0.24429 | 0.14712 | 0 | 4.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46
Single | Manufacturer | 1800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0033 | 0 | 0 | 0 | 4.14 | 10.1788 | 1.2354 | 0.39199 | 0.12137 | 0 | 4.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 66
Single | Manufacturer | 1800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026 | 0 | 0 | 0 | 4.96 | 10.1788 | 0.97337 | 0.46964 | 0.095628 | 0 | 4.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 67
Single | Manufacturer | 1800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0 | 5.4 | 10.1788 | 0.74875 | 0.5113 | 0.07356 | 0 | 4.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 64
Single | Manufacturer | 2700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.006 | 0 | 0 | 0 | 5.77 | 15.2681 | 2.2462 | 0.24281 | 0.14712 | 0 | 4.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 52
Single | Manufacturer | 2700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0 | 0 | 0 | 9.12 | 15.2681 | 1.8719 | 0.38379 | 0.1226 | 0 | 4.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 71
Single | Manufacturer | 2700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004 | 0 | 0 | 0 | 11 | 15.2681 | 1.4975 | 0.4629 | 0.09808 | 0 | 4.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 73
Single | Manufacturer | 2700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 12.1 | 15.2681 | 1.1231 | 0.50919 | 0.07356 | 0 | 4.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 69
Single | Manufacturer | 2700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0 | 12.8 | 15.2681 | 0.74875 | 0.53865 | 0.04904 | 0 | 4.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 58
Single | Manufacturer | 3600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008 | 0 | 0 | 0 | 10.3 | 20.3575 | 2.995 | 0.24381 | 0.14712 | 0 | 4.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 52
Single | Manufacturer | 3600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0067 | 0 | 0 | 0 | 16.1 | 20.3575 | 2.5083 | 0.38111 | 0.12321 | 0 | 4.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 71
Single | Manufacturer | 3600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0054 | 0 | 0 | 0 | 19.2 | 20.3575 | 2.0216 | 0.45449 | 0.099306 | 0 | 4.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 73
Single | Manufacturer | 3600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004 | 0 | 0 | 0 | 21.6 | 20.3575 | 1.4975 | 0.5113 | 0.07356 | 0 | 4.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 69
Single | Manufacturer | 3600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0027 | 0 | 0 | 0 | 22.8 | 20.3575 | 1.0108 | 0.5397 | 0.049653 | 0 | 4.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 59
Parallel | Fully open | 2700 | 2.87 | 2.72 | 0 | 12.46 | 12.28 | 12.79 | 12.51 | 0.0072662 | 10.1058 | 9.5776 | 9.8417 | 11.257 | 15.2681 | 2.7203 | 0.47372 | 0.17817 | 0.25865 | 4.3027 | 0.64252 | 0.01 | 0.6426 | 0.00037324 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.035212 | 0.035212 | 0.024899 | 0.14751 | 0 | 0.13973 | 0.0062076 | 0.0091519
Parallel | Partial 1 | 2700 | 3.08 | 2.96 | 0 | 14.49 | 14.49 | 14.42 | 14.4667 | 0.0062834 | 10.8453 | 10.4227 | 10.634 | 11.6923 | 15.2681 | 2.3524 | 0.49204 | 0.15407 | 0.040415 | 4.3027 | 0.1004 | 0.01 | 0.10089 | 4.3821e-05 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.035212 | 0.035212 | 0.024899 | 0.028946 | 0 | 0.016406 | 0.0012181 | 0.0010745
Parallel | Partial 2 | 2700 | 3.52 | 3.53 | 0 | 41.05 | 40.99 | 40.99 | 41.01 | 0.0022165 | 12.3946 | 12.4298 | 12.4122 | 12.5439 | 15.2681 | 0.82981 | 0.52787 | 0.054349 | 0.034641 | 4.3027 | 0.086053 | 0.01 | 0.086632 | 4.6824e-06 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.035212 | 0.035212 | 0.024899 | 0.024905 | 0 | 0.001753 | 0.001048 | 0.00011481
Parallel | Closed | 2700 | 3.55 | 3.55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.5002 | 12.5002 | 12.5002 | 12.5002 | 15.2681 | 0 | 0.52604 | 0 | 0 | 4.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.035212 | 0.035212 | 0.024899 | 0.024899 | 0 | 0 | 0.0010478 | 0
Series | Fully open | 2700 | 0.68 | 1.68 | 0 | 16.64 | 16.17 | 16.03 | 16.28 | 0.0055836 | 2.3944 | 5.9156 | 8.31 | 9.1457 | 15.2681 | 2.0903 | 0.38487 | 0.13691 | 0.31953 | 4.3027 | 0.79376 | 0.01 | 0.79382 | 0.00027226 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.035212 | 0.035212 | 0.049797 | 0.095506 | 0 | 0.10193 | 0.0040191 | 0.0066757
Series | Partial 1 | 2700 | 0.9 | 1.84 | 0 | 16.71 | 16.58 | 16.76 | 16.6833 | 0.0054486 | 3.1691 | 6.479 | 9.6481 | 10.4438 | 15.2681 | 2.0398 | 0.4395 | 0.1336 | 0.092916 | 4.3027 | 0.23082 | 0.01 | 0.23103 | 7.5452e-05 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.035212 | 0.035212 | 0.049797 | 0.054456 | 0 | 0.028247 | 0.0022916 | 0.0018501
Series | Partial 2 | 2700 | 2.89 | 3.26 | 0 | 30.52 | 30.23 | 30.67 | 30.4733 | 0.0029829 | 10.1762 | 11.4791 | 21.6553 | 21.8938 | 15.2681 | 1.1167 | 0.92134 | 0.073142 | 0.22368 | 4.3027 | 0.55566 | 0.01 | 0.55575 | 5.44e-05 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.035212 | 0.035212 | 0.049797 | 0.050551 | 0 | 0.020366 | 0.0021273 | 0.0013339
Series | Closed | 2700 | 3.52 | 3.55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.3946 | 12.5002 | 24.8948 | 24.8948 | 15.2681 | 0 | 1.0476 | 0 | 0 | 4.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.035212 | 0.035212 | 0.049797 | 0.049797 | 0 | 0 | 0.0020956 | 0
beta_2 | 33 | [8 empty] | elevation err | 0.021631
cot(beta_2) | 1.5399 | [8 empty] | average head | 9.2461
|  | Actual |  |  | Theoretrical
|  | Volumetric Flow | Transducer Head | Corrected Head | Volumetric Flow | Transducer Head | Corrected Head
Parallel | Fully open | 0.0072662 | 9.8417 | 11.257 | 0.009715 | 5.2818 | 7.8117
Parallel | Partial 1 | 0.0062834 | 10.634 | 11.6923 | 0.0094985 | 5.7043 | 8.1227
Parallel | Partial 2 | 0.0022165 | 12.4122 | 12.5439 | 0.0058226 | 10.3523 | 11.2611
Parallel | Closed | 0 | 12.5002 | 12.5002 | 0 | 12.3946 | 12.3946
Series | Fully open | 0.0055836 | 8.31 | 9.1457 | 0.0048575 | 10.5636 | 11.1961
Series | Partial 1 | 0.0054486 | 9.6481 | 10.4438 | 0.0047492 | 11.4087 | 12.0133
Series | Partial 2 | 0.0029829 | 21.6553 | 21.8938 | 0.0029113 | 20.7046 | 20.9318
Series | Closed | 0 | 24.8948 | 24.8948 | 0 | 24.7892 | 24.7892
Geometrically Similar | Impeller Diameter | $b$ | $w$ | Volumetric Flow | Pump Speed | Head | Pump Eff | Impeller Speed, $U$ | Radial Exit Velocity, $v_{2r}$ | Head Coefficient, $\Psi$ | Flow Coefficient, $\Phi$
|  | (m) | (m) | (m$^3$/s) | (RPM) | (m) | (%) | (m/s) | (m/s)
No | 0.108 | 0.009 | 0.0085 | 0.008 | 3600 | 10.3 | 52 | 20.3575 | 2.995 | 0.24381 | 0.14712
No | 0.108 | 0.009 | 0.0085 | 0.0067 | 3600 | 16.1 | 71 | 20.3575 | 2.5083 | 0.38111 | 0.12321
No | 0.108 | 0.009 | 0.0085 | 0.0054 | 3600 | 19.4 | 73 | 20.3575 | 2.0216 | 0.45922 | 0.099306
No | 0.108 | 0.009 | 0.0085 | 0.004 | 3600 | 21.6 | 69 | 20.3575 | 1.4975 | 0.5113 | 0.07356
No | 0.108 | 0.009 | 0.0085 | 0.0027 | 3600 | 22.8 | 59 | 20.3575 | 1.0108 | 0.5397 | 0.049653
No | 0.102 | 0.009 | 0.0085 | 0.0076 | 3600 | 7.9 | 47 | 19.2265 | 3.0382 | 0.20965 | 0.15802
No | 0.102 | 0.009 | 0.0085 | 0.0063 | 3600 | 13 | 66 | 19.2265 | 2.5185 | 0.34499 | 0.13099
No | 0.102 | 0.009 | 0.0085 | 0.005 | 3600 | 16.3 | 69 | 19.2265 | 1.9988 | 0.43257 | 0.10396
No | 0.102 | 0.009 | 0.0085 | 0.0038 | 3600 | 18 | 64 | 19.2265 | 1.5191 | 0.47768 | 0.079011
No | 0.102 | 0.009 | 0.0085 | 0.0025 | 3600 | 19.2 | 54 | 19.2265 | 0.99941 | 0.50953 | 0.051981
No | 0.096 | 0.009 | 0.0085 | 0.0071 | 3600 | 6.65 | 45 | 18.0956 | 3.0448 | 0.19923 | 0.16826
No | 0.096 | 0.009 | 0.0085 | 0.0059 | 3600 | 11 | 62 | 18.0956 | 2.5302 | 0.32955 | 0.13982
No | 0.096 | 0.009 | 0.0085 | 0.0047 | 3600 | 13.9 | 65 | 18.0956 | 2.0156 | 0.41643 | 0.11139
No | 0.096 | 0.009 | 0.0085 | 0.0035 | 3600 | 15.8 | 60 | 18.0956 | 1.501 | 0.47335 | 0.082946
No | 0.096 | 0.009 | 0.0085 | 0.0024 | 3600 | 16.8 | 52 | 18.0956 | 1.0292 | 0.50331 | 0.056878
No | 0.083 | 0.009 | 0.0085 | 0.0059 | 3600 | 2.57 | 24 | 15.6451 | 3.0037 | 0.103 | 0.19199
No | 0.083 | 0.009 | 0.0085 | 0.0049 | 3600 | 5.95 | 43 | 15.6451 | 2.4946 | 0.23847 | 0.15945
No | 0.083 | 0.009 | 0.0085 | 0.0039 | 3600 | 8.41 | 53 | 15.6451 | 1.9855 | 0.33706 | 0.12691
No | 0.083 | 0.009 | 0.0085 | 0.0029 | 3600 | 9.91 | 51 | 15.6451 | 1.4764 | 0.39718 | 0.094366
No | 0.083 | 0.009 | 0.0085 | 0.002 | 3600 | 10.5 | 38 | 15.6451 | 1.0182 | 0.42082 | 0.06508
Yes | 0.108 | 0.009 | 0.0085 | 0.008 | 3600 | 10.3 | 52 | 20.3575 | 2.995 | 0.24381 | 0.14712
Yes | 0.108 | 0.009 | 0.0085 | 0.0067 | 3600 | 16.1 | 71 | 20.3575 | 2.5083 | 0.38111 | 0.12321
Yes | 0.108 | 0.009 | 0.0085 | 0.0054 | 3600 | 19.4 | 73 | 20.3575 | 2.0216 | 0.45922 | 0.099306
Yes | 0.108 | 0.009 | 0.0085 | 0.004 | 3600 | 21.6 | 69 | 20.3575 | 1.4975 | 0.5113 | 0.07356
Yes | 0.108 | 0.009 | 0.0085 | 0.0027 | 3600 | 22.8 | 59 | 20.3575 | 1.0108 | 0.5397 | 0.049653
Yes | 0.102 | 0.0085 | 0.0080278 | 0.0076 | 3600 | 7.9 | 47 | 19.2265 | 3.1898 | 0.20965 | 0.16591
Yes | 0.102 | 0.0085 | 0.0080278 | 0.0063 | 3600 | 13 | 66 | 19.2265 | 2.6442 | 0.34499 | 0.13753
Yes | 0.102 | 0.0085 | 0.0080278 | 0.005 | 3600 | 16.3 | 69 | 19.2265 | 2.0986 | 0.43257 | 0.10915
Yes | 0.102 | 0.0085 | 0.0080278 | 0.0038 | 3600 | 18 | 64 | 19.2265 | 1.5949 | 0.47768 | 0.082954
Yes | 0.102 | 0.0085 | 0.0080278 | 0.0025 | 3600 | 19.2 | 54 | 19.2265 | 1.0493 | 0.50953 | 0.054575
Yes | 0.096 | 0.008 | 0.0075556 | 0.0071 | 3600 | 6.65 | 45 | 18.0956 | 3.3641 | 0.19923 | 0.18591
Yes | 0.096 | 0.008 | 0.0075556 | 0.0059 | 3600 | 11 | 62 | 18.0956 | 2.7955 | 0.32955 | 0.15449
Yes | 0.096 | 0.008 | 0.0075556 | 0.0047 | 3600 | 13.9 | 65 | 18.0956 | 2.2269 | 0.41643 | 0.12307
Yes | 0.096 | 0.008 | 0.0075556 | 0.0035 | 3600 | 15.8 | 60 | 18.0956 | 1.6584 | 0.47335 | 0.091644
Yes | 0.096 | 0.008 | 0.0075556 | 0.0024 | 3600 | 16.8 | 52 | 18.0956 | 1.1372 | 0.50331 | 0.062842
Yes | 0.083 | 0.0069167 | 0.0065324 | 0.0059 | 3600 | 2.57 | 24 | 15.6451 | 3.7398 | 0.103 | 0.23904
Yes | 0.083 | 0.0069167 | 0.0065324 | 0.0049 | 3600 | 5.95 | 43 | 15.6451 | 3.1059 | 0.23847 | 0.19852
Yes | 0.083 | 0.0069167 | 0.0065324 | 0.0039 | 3600 | 8.41 | 53 | 15.6451 | 2.4721 | 0.33706 | 0.15801
Yes | 0.083 | 0.0069167 | 0.0065324 | 0.0029 | 3600 | 9.91 | 51 | 15.6451 | 1.8382 | 0.39718 | 0.11749
Yes | 0.083 | 0.0069167 | 0.0065324 | 0.002 | 3600 | 10.5 | 38 | 15.6451 | 1.2677 | 0.42082 | 0.08103
ideal shutoff head | 42.2455
thumb | 21.1228
actual shutoff head | 21.761